## Switch HSR-PRP(NO RJ45)
EMPRESA ELECTRICA REGIONAL DEL SUR S.A. |  |  |  | EERSSA
FORMULARIO DE ESPECIFICACIONES TECNICAS |  |  |  | Mayo-2023
Switch de comunicación (HSR/PRP, HSR-PRP RedBox, HSR QuadBox) (3 puerto FO)
No. | DESCRIPCIÓN | ESPECIFICACIONES / CERTIFICADOS / NORMAS SOLICITADAS | ESPECIFICACIONES / CERTIFICADOS / NORMAS OFERTADAS | UBICACIÓN DE INFORMACIÓN (# DE FOLIO OFERTA) *
0 | Cantidad
0.2 | Marca: | Indicar
0.3 | Modelo o Número de parte: | Indicar
0.4 | Páis de procedencia o fabricación: | Indicar
1 | Ethernet Interface Redundancy
1.1 | Port A: 100 Base-FX (LC/UPC/1310nm-Multi Mode ≤2Km) | 1 (to connect to a Parallel Redundancy Protocol-PRP network or a High-Availability Seamless Redundancy-HSR ring)
1.2 | Port B: 100 Base-FX (LC/UPC/1310nm-Multi Mode ≤2Km) | 1 (to connect to a Parallel Redundancy Protocol-PRP network or a High-Availability Seamless Redundancy-HSR ring)
1.3 | Port L (Coupler or Interlink) 100 Base-FX (LC/UPC/Multi Mode ≤2Km) | 1 - To connect a SAN (Singly Attached Node) to an HSR ring via an HSR device. - To connect an HSR ring to a PRP network and viceversa - To connect an HSR ring to an RSTP network
2 | Manager Interface
2.1 | Console Port | 1 Ethernet console (10/100/1000Mbps RJ45) or USB Type-B
3 | Product Specifications
3.1 | Standards | IEEE 802.3 for 10BaseT IEEE 802.3ab for 1000BaseT(X) IEEE 802.3u for 100BaseT(X) and 100BaseFX IEEE 802.3z for 1000BaseSX/LX/LHX/ZX IEC62439-3-5(HSR, Edition 3.0 update ready, Modos: HSR-SAN,PRP-HSR, HSR-HSR) IEC62439-3-4(PRP, Edition 3.0 update ready, Modos: Duplicate discard, diplicate accept, transparent reception, PRP-HSR)
3.2 | Power Requirements | Power input: 100-240VAC, 60Hz (includes power adapter if needed) Power consumption：<8W Overload protection：Support Reverse connection protection：Support
3.3 | Physical Characteristics | Housing：Metal Cooling：Natural cooling, fanless Protection Class：IP40 Dimensions(WxHxD)：indicate Weight：indicate Mounting：Din-rail or panel mounting
3.4 | Environmental limits | Operating temperature: -35°C to +80°C Storage temperature: -35°C to +80°C Ambient Relative Humidity: 10% - 90% (non-condensing)
3.5 | Approvals | CE, FCC EMC: EN 55032/35, EN 61000-6-4, EN 61000-6-2 Rail Traffic: EN 50121-4 IEC61850-3, IEEE1613 IEC 62368-1, EN 62368-1
3.6 | Industry standard | IEC61000-4-2(ESD) ±8kV(contact),±15kV(air) IEC61000-4-3(RS) 10V/m(80MHz-2GHz) IEC61000-4-4(EFT) Power Port:±4kV;Data Port:±2kV IEC61000-4-5(Surge) Power Port:±2kV/DM,±4kV/CM;Data Port:±2kV IEC61000-4-6(CS) 3V(10kHz-150kHz);10V(150kHz-80MHz) IEC61000-4-16(common mode conduction) 30V(cont.),300V(1s)
4 | Ethernet Software Features
4.1 | Redundancy protocol | HSR and the recovery time is 0 ms PRP and the recovery time is 0 ms PRP/HSR Coupling Quadbox mode
4.2 | Management and maintenance | Console and Web management Telnet CLI SNMPv1/v2c SNMPv3 LLDP DHCP client software update configuration download configuration upload FTP Syslog Port speed auto-negotiation
4.3 | Time synchronization | PTPv2(IEEE1588-2008) transparent precision<1us NTP server/client SNTP
4.4 | Security | HTTPS/SSL, TACACS+, RADIUS, SSH, Trust access control
5 | Software
5.1 | Includes configuration software, perpetually licensed for PC by EERSSA | Include
6 | Referencia
NOTA *: La indicación de los datos técnicos ofertados, deben ser resaltados en la oferta a ser presentada, indicando el número de folio respectivo. La falta de esta información no permitirá corroborar lo ofrecido y será motivo de descalificación. No es aceptable que se indique un rango amplio de páginas o rango de folio, la información debe ser concreta y específica, que permita verificar el cumplimiento de especificaciones técnicas.